## MCC
BOM FOR MCC PANEL
SR NO. | ITEM DESCRIPTIONS | MAKE | PART NO | ITEM QTY | FDR QTY | TOTAL QTY | UOM
A | MAIN INCOMER, MCCB 3P,200 AMP |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 3P,200 AMP 55KA | Siemens | 3VM1220-5EE32-0AA0 | 1 | 1 | 1 | Nos.
2 | Extended Rotary Handle for MCCB | Siemens | 3VM9217-0FK51 | 1 | 1 | 1 | Nos.
3 | Sprederer Link + Phase barrier | Siemens | 3VM9253-0QC50 | 2 | 1 | 2 | Set.
4 | Shunt Release Coil 230vac | Siemens | 3VM9908-0BL33 | 1 | 1 | 1 | Nos.
5 | Auxiliary Switch AUX (1 C/O) | Siemens | 3VM9988-0AA12 | 1 | 1 | 1 | Nos.
6 | Trip Alarm Switch TAS (1 C/O) | Siemens | 3VM9988-0AB12 | 1 | 1 | 1 | Nos.
7 | 2A, 1P, 10kA, C-Curve MCB | Siemens | 5SL41027RC | 4 | 1 | 4 | Nos.
8 | 6A, 1P, 10kA, C-Curve MCB | Siemens | 5SL41067RC | 2 | 1 | 2 | Nos.
9 | 10A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42107RC | 2 | 1 | 2 | Nos.
10 | 6A, 3P, 10kA, C-Curve MCB | Siemens | 5SL43067RC | 1 | 1 | 1 | Nos.
11 | Digital Ammeter (0-200 Amp) | Rishabh |  | 1 | 1 | 1 | Nos.
12 | Digital Voltmeter (0-500 Volt) | Rishabh |  | 1 | 1 | 1 | Nos.
13 | Ammeter Selecter Switch | Salzer |  | 1 | 1 | 1 | Nos.
14 | Voltmeter Selector Switch | Salzer |  | 1 | 1 | 1 | Nos.
15 | Digital MFM- EM 6436 With RS 485 Communication | Conzerv | EM 6436 | 1 | 1 | 1 | Nos.
16 | Current Transformer 200/5 15VA resin cast | Sahara |  | 3 | 1 | 3 | Nos.
17 | Red Indication Lamp, 230VAC supply voltage | Teknic | 3PLBR4L | 2 | 1 | 2 | Nos.
18 | Yellow Indication Lamp, 230VAC supply voltage | Teknic | 3PLBR8L | 1 | 1 | 1 | Nos.
19 | Blue Indication Lamp, 230VAC supply voltage | Teknic | 3PLBR6L | 1 | 1 | 1 | Nos.
20 | Green Indication lamp, 230VAC supply voltage | Teknic | 3PLBR3L | 2 | 1 | 2 | Nos.
21 | Amber Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
22 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | MY2N | 3 | 1 | 3 | Nos.
23 | Aux. contactor 3P,9Amp with coil voltage 230VAC | Siemens | 3RT2016 | 6 | 1 | 6 | Nos.
24 | Add On Block 4 NO | Siemens | 3RH2911-1FA40 | 6 | 1 | 6 | Nos.
25 | CTTB | STD. |  | 4 | 1 | 4 | Nos.
26 | Neutral Link | STD. |  | 3 | 1 | 3 | Nos.
27 | E.STOP PB Mh. Type. With 1 NO Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
28 | Control Transformer 1.5 KVA, 415/230Vac | Sahara |  | 1 | 1 | 1 | Nos.
29 | L/R 3 Position SSW | Salzer |  | 1 | 1 | 1 | Nos.
30 | Door Limit Switch | Kaycee |  | 2 | 1 | 2 | Nos.
31 | 5watt, Tubelight | Oreva |  | 2 | 1 | 2 | Nos.
32 | 6 Inch Air Filter | Elettro |  | 6 | 1 | 6 | Nos.
33 | 6 Inch Fan | Rexnord |  | 3 | 1 | 3 | Nos.
34 | Control terminals 4Sq.mm, Red | Elmex |  | 5 | 1 | 5 | Nos.
35 | Control terminals 4Sq.mm, Black | Elmex |  | 5 | 1 | 5 | Nos.
36 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 6 | 1 | 6 | Nos.
37 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
38 | End Plate | Elmex |  | 5 | 1 | 5 | Nos.
39 | TB Marker (1-10) | Elmex |  | 5 | 1 | 5 | Nos.
1 | VFD FEEDER 0.37 KW 1 NOS (FEED PUMP) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 2.5 Amp | Siemens | 3RV2311-1CC10 | 1 | 1 | 1 | Nos.
2 | Fuse Base 160 AMP | Siemens | 3NH3032-0RC | 3 | 1 | 3 | Nos.
3 | Fuse Link 6 Amp | Siemens | 3NA78010RC | 3 | 1 | 3 | Nos.
4 | VFD 0.75kW | STD. | Free Issue From Client | 1 | 1 | 1 | Nos.
5 | Aux contactor 3P,9Amp with coil voltage 230VAC | Siemens | 3RT2016 | 1 | 1 | 1 | Nos.
6 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
7 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
8 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
9 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
10 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
11 | Aux. relay 4 c/o with base & pin, 230VAC | Omron |  | 2 | 1 | 2 | Nos.
12 | L/R 3 Position SSW | Salzer |  | 1 | 1 | 1 | Nos.
13 | Yellow PB for Speed Increase with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
14 | Blue PB for Speed Decrease with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
15 | Power cable 2.5Sq.mm, RYB | Polycab |  | 13 | 1 | 13 | Mtrs
16 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
17 | Power terminals 6Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
18 | Power terminals 6Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
19 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 18 | 1 | 18 | Nos.
20 | TB Flag | Elmex |  | 5 | 1 | 5 | Nos.
21 | End Plate | Elmex |  | 5 | 1 | 5 | Nos.
22 | TB Marker (1-10) | Elmex |  | 5 | 1 | 5 | Nos.
2 | VFD FEEDER 2.2 KW 1 NOS (ATOMIZER) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 6.3 Amp | Siemens | 3RV2311-1GC10 | 1 | 1 | 1 | Nos.
2 | Fuse Base 160 AMP | Siemens | 3NH3032-0RC | 3 | 1 | 3 | Nos.
3 | Fuse Link 10 Amp | Siemens | 3NA78030RC | 3 | 1 | 3 | Nos.
4 | VFD 2.2kW | STD. | Free Issue From Client | 1 | 1 | 1 | Nos.
5 | Aux contactor 3P,9Amp with coil voltage 230VAC | Siemens | 3RT2016 | 1 | 1 | 1 | Nos.
6 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
7 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
8 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
9 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
10 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
11 | Aux. relay 4 c/o with base & pin, 230VAC | Omron |  | 2 | 1 | 2 | Nos.
13 | L/R 3 Position SSW | Salzer |  | 1 | 1 | 1 | Nos.
14 | Yellow PB for Speed Increase with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
15 | Blue PB for Speed Decrease with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
16 | Power cable 2.5Sq.mm, RYB | Polycab |  | 13 | 1 | 13 | Mtrs
17 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
18 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
19 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
20 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 18 | 1 | 18 | Nos.
21 | TB Flag | Elmex |  | 5 | 1 | 5 | Nos.
22 | End Plate | Elmex |  | 5 | 1 | 5 | Nos.
23 | TB Marker (1-10) | Elmex |  | 5 | 1 | 5 | Nos.
3 | VFD FEEDER 9.3 KW 1 NOS (ID BLOWER) |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 32 Amp | Siemens | 3VM1132-5MH32-0AA0 | 1 | 1 | 1 | Nos.
2 | Fuse Base 160 AMP | Siemens | 3NH3032-0RC | 3 | 1 | 3 | Nos.
3 | Fuse Link 32 Amp | Siemens | 3NA78120RC | 3 | 1 | 3 | Nos.
4 | VFD 9.3kW | STD. | Free Issue From Client | 1 | 1 | 1 | Nos.
5 | Aux contactor 3P,9Amp with coil voltage 230VAC | Siemens |  | 1 | 1 | 1 | Nos.
6 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
7 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
8 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
9 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
10 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
11 | Aux. relay 4 c/o with base & pin, 230VAC | Omron |  | 2 | 1 | 2 | Nos.
13 | L/R 3 Position SSW | Salzer |  | 1 | 1 | 1 | Nos.
14 | Yellow PB for Speed Increase with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
15 | Blue PB for Speed Decrease with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
16 | Power cable 2.5Sq.mm, RYB | Polycab |  | 13 | 1 | 13 | Mtrs
17 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
18 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
19 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
20 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 18 | 1 | 18 | Nos.
21 | TB Flag | Elmex |  | 5 | 1 | 5 | Nos.
22 | End Plate | Elmex |  | 5 | 1 | 5 | Nos.
23 | TB Marker (1-10) | Elmex |  | 5 | 1 | 5 | Nos.
4 | THYRISOR FEEDER 20 KW 1 NOS (ELECTRICAL HEATER-01) |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 80 Amp | Siemens | 3VM1180-5MH32-0AA0 | 1 | 1 | 1 | Nos.
2 | Thyristor 20kW | STD. | Free Issue From Client | 1 | 1 | 1 | Nos.
3 | Power contactor 3P,65Amp with coil voltage 230VAC | Siemens | 3RT2037 | 1 | 1 | 1 | Nos.
4 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Digital Ammeter (0-75 Amp) | L&T |  | 1 | 1 | 1 | Nos.
7 | Current Transformer 75/5VA | Elmex |  | 1 | 1 | 1 | Nos.
8 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
9 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
10 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
11 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
12 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
13 | Power cable 16Sq.mm, BLACK | Polycab |  | 13 | 1 | 13 | Mtrs
14 | Power terminals 25Sq.mm, Gray | Elmex |  | 3 | 1 | 3 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 13 | 1 | 13 | Nos.
16 | TB Flag | Elmex |  | 5 | 1 | 5 | Nos.
17 | End Plate | Elmex |  | 5 | 1 | 5 | Nos.
18 | TB Marker (1-10) | Elmex |  | 5 | 1 | 5 | Nos.
5 | DOL FEEDER 0.25 KW 1 NOS (FORCE LUB OIL PUMP) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 1A | Siemens | 3RV2311-0JC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,7Amp with coil voltage 230VAC | Siemens | 3RT2015 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 0.45-0.63A | Siemens | 3RU2116-0GB0 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 6Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 6Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
6 | DOL FEEDER 0.4 KW 1 NOS (BURNER) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 1.6A | Siemens | 3RV2311-1AC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,7Amp with coil voltage 230VAC | Siemens | 3RT2015 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
5 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
6 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
7 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
8 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
9 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
10 | Power terminals 6Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
11 | Power terminals 6Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
12 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 10 | 1 | 10 | Nos.
13 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
14 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
15 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
7 | DOL FEEDER 0.4 KW 1 NOS (IBFD ROTARY VALVE) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 1.6A | Siemens | 3RV2311-1AC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,7Amp with coil voltage 230VAC | Siemens | 3RT2015 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 1.1-1.6A | Siemens | 3RU2116-1AB0 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 6Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 6Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
8 | DOL FEEDER 0.4 KW 1 NOS (CYCLONE ROTARY VALVE) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 1.6A | Siemens | 3RV2311-1AC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,7Amp with coil voltage 230VAC | Siemens | 3RT2015 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 1.1-1.6A | Siemens | 3RU2116-1AB0 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 6Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 6Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
9 | RDOL FEEDER 0.75 KW 1 NOS (CIP WINCH) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 2.5A | Siemens | 3RV2311-1CC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,7Amp with coil voltage 230VAC | Siemens | 3RT2015 | 2 | 1 | 2 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 2 | 1 | 2 | Nos.
4 | Overload Relay 1.4-2A | Siemens | 3RU2116-1BB0 | 1 | 1 | 1 | Nos.
4 | Overload Mounting kit | Siemens | 3RU2916-3AA01 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 2 | 1 | 2 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 6Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 6Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 16 | 1 | 16 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
10 | DOL FEEDER 1.5 KW 1 NOS (IBFD BLOWER) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 4A | Siemens | 3RV2311-1EC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,7Amp with coil voltage 230VAC | Siemens | 3RT2015 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 2.8-4A | Siemens | 3RU2116-1EB0 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 6Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 6Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
11 | DOL FEEDER 2.2 KW 1 NOS (SCRUBBER PUMP) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 6.3A | Siemens | 3RV2311-1GC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,12Amp with coil voltage 230VAC | Siemens | 3RT2017 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 4.5-6.3A | Siemens | 3RU2116-1GB00 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
12 | DOL FEEDER 2.2 KW 1 NOS (ROOT BLOWER) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 6.3A | Siemens | 3RV2311-1GC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,12Amp with coil voltage 230VAC | Siemens | 3RT2017 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 4.5-6.3A | Siemens | 3RU2116-1GB00 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
13 | DOL FEEDER 2.2 KW 1 NOS (SPARE-01) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 6.3A | Siemens | 3RV2311-1GC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,12Amp with coil voltage 230VAC | Siemens | 3RT2017 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 4.5-6.3A | Siemens | 3RU2116-1GB00 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
14 | DOL FEEDER 3.7 KW 1 NOS (FD BLOWER) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 10A | Siemens | 3RV2311-1JC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,25Amp with coil voltage 230VAC | Siemens | 3RT2026 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 7-10A | Siemens | 3RU2126-1JB0 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
15 | DOL FEEDER 3.7 KW 1 NOS (CIRCULATION PUMP) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 10A | Siemens | 3RV2311-1JC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,25Amp with coil voltage 230VAC | Siemens | 3RT2026 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 7-10A | Siemens | 3RU2126-1JB0 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
16 | DOL FEEDER 3.7 KW 1 NOS (SPARE-02) |  |  | 1 | 1 | 1 | Nos.
1 | MPCB 10A | Siemens | 3RV2311-1JC10 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,25Amp with coil voltage 230VAC | Siemens | 3RT2026 | 1 | 1 | 1 | Nos.
3 | 3NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA31 | 1 | 1 | 1 | Nos.
4 | Overload Relay 7-10A | Siemens | 3RU2126-1JB0 | 1 | 1 | 1 | Nos.
5 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
11 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
12 | Power terminals 10Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
13 | Power terminals 10Sq.mm, Yellow | Elmex |  | 1 | 1 | 1 | Nos.
14 | Power terminals 10Sq.mm, Blue | Elmex |  | 1 | 1 | 1 | Nos.
15 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
16 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
17 | End Plate | Elmex |  | 4 | 1 | 4 | Nos.
18 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
17 | S/D FEEDER 7.5 KW 1 NOS (CIP PUMP) |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 3P 32AMP | Siemens | 3VM1132-5MH32-0AA0 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,25Amp with coil voltage 230VAC | Siemens | 3RT2026 | 2 | 1 | 2 | Nos.
3 | Power contactor 3P,12Amp with coil voltage 230VAC | Siemens | 3RT2018 | 1 | 1 | 1 | Nos.
4 | 2NO And 2NC contact block As per requirement | Siemens | 3RH2911-1HA22 | 2 | 1 | 2 | Nos.
5 | 1NO And 1NC contact block As per requirement | Siemens | 3RH2911-1HA11 | 1 | 1 | 1 | Nos.
6 | Overload Relay 7-10A | Siemens | 3RU2126-1JB0 | 1 | 1 | 1 | Nos.
7 | Digital Ammeter (0-30 Amp) | Rishabh |  | 1 | 1 | 1 | Nos.
8 | Current Transformer 30/5A | Elmex |  | 1 | 1 | 1 | Nos.
9 | 2A, 1P, 10kA, C-Curve MCB- Control supply | Siemens | 5SL41027RC | 1 | 1 | 1 | Nos.
10 | S/D timer 0-60 Sec | GIC |  | 1 | 1 | 1 | Nos.
11 | Neutral Link | STD. |  | 1 | 1 | 1 | Nos.
12 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
13 | Stop PB Mh. Head with NC Contact | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
14 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
15 | Aux. relay 2 c/o with base & pin, 230VAC | Omron |  | 1 | 1 | 1 | Nos.
16 | Power cable 4Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
17 | Power cable 2.5Sq.mm, RYB | Polycab |  | 6 | 1 | 6 | Mtrs
18 | Power terminals 10Sq.mm, Red | Elmex |  | 2 | 1 | 2 | Nos.
19 | Power terminals 10Sq.mm, Yellow | Elmex |  | 2 | 1 | 2 | Nos.
20 | Power terminals 10Sq.mm, Blue | Elmex |  | 2 | 1 | 2 | Nos.
21 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 11 | 1 | 11 | Nos.
22 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
23 | End Plate | Elmex |  | 5 | 1 | 5 | Nos.
24 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.
18 | PLC PANEL SUPPLY |  |  | 1 | 1 | 1 | Nos.
1 | 16A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42167RC | 1 | 1 | 1 | Nos.
2 | Power terminals 6Sq.mm, Red | Elmex |  | 1 | 1 | 1 | Nos.
3 | Power terminals 6Sq.mm, BLACK | Elmex |  | 1 | 1 | 1 | Nos.
19 | HAMMER 5 NOS. |  |  | 1 | 5 | 5 | Nos.
1 | 16A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42167RC | 1 | 5 | 5 | Nos.
2 | 6A, 1P, 10kA, C-Curve MCB | Siemens | 5SL41067RC | 1 | 1 | 1 | Nos.
3 | Power contactor 3P,12Amp with coil voltage 230VAC | Siemens | 3RT2018 | 1 | 5 | 5 | Nos.
4 | Start (Green) Illuminated Push button with NO Contact | Teknic | 2ALRF3 | 1 | 5 | 5 | Nos.
5 | 6 POINT SEQUENTIAL TIMER | EAPL |  | 1 | 1 | 1 | Nos.
6 | Power terminals 6Sq.mm, Red | Elmex |  | 4 | 1 | 4 | Nos.
7 | Power terminals 6Sq.mm,YELLOW | Elmex |  | 4 | 1 | 4 | Nos.
8 | Power terminals 6Sq.mm, BLUE | Elmex |  | 4 | 1 | 4 | Nos.
9 | Control terminals 2.5Sq.mm, Gray | Elmex |  | 4 | 1 | 4 | Nos.
10 | TB Flag | Elmex |  | 4 | 1 | 4 | Nos.
11 | End Plate | Elmex |  | 5 | 1 | 5 | Nos.
12 | TB Marker (1-10) | Elmex |  | 4 | 1 | 4 | Nos.

## PLC
BOM FOR PLC PANEL
SR NO. | ITEM DESCRIPTIONS | MAKE | PART NO | ITEM QTY | FDR QTY | TOTAL QTY | UOM
A | MAIN INCOMER, MAIN SWITCH 3P,32 AMP |  |  | 1 | 1 | 1 | Nos.
1 | MAIN SWITCH 3P, 32AMP | Salzer |  | 1 | 1 | 1 | Nos.
2 | 32A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42327RC | 1 | 1 | 1 | Nos.
3 | 6A, 1P, 10kA, C-Curve MCB | Siemens | 5SL41067RC | 3 | 1 | 3 | Nos.
4 | 6A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42067RC | 5 | 1 | 5 | Nos.
5 | 10A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42107RC | 2 | 1 | 2 | Nos.
6 | 20A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42207RC | 3 | 1 | 3 | Nos.
7 | 40A, 2P, 10kA, C-Curve MCB | Siemens | 5SL42407RC | 1 | 1 | 1 | Nos.
8 | Fuse Terminals with 2Amp Fuse | Elmex |  | 10 | 1 | 10 | Nos.
9 | 230VAC On Indication (RED) | Teknic | 3PLBR4L | 1 | 1 | 1 | Nos.
10 | 24VDC On Indication (GREEN) | Teknic | 3PLBR3L | 4 | 1 | 4 | Nos.
11 | 24VDC, 10AMP SMPS Module | Siemens |  | 2 | 1 | 2 | Nos.
12 | 24VDC, 20AMP SMPS Module | Siemens |  | 2 | 1 | 2 | Nos.
13 | 24VDC, 20AMP Redundancy Module | Weidmuller |  | 1 | 1 | 1 | Nos.
14 | 24VDC, 40AMP Redundancy Module | Weidmuller |  | 1 | 1 | 1 | Nos.
15 | 6Sq.mm Control Terminals (Blue) | Elmex |  | 5 | 1 | 5 | Nos.
16 | 6Sq.mm Control Terminals (Grey) | Elmex |  | 5 | 1 | 5 | Nos.
17 | 4Sq.mm Control Terminals (Blue) | Elmex |  | 10 | 1 | 10 | Nos.
18 | 4Sq.mm Control Terminals (Grey) | Elmex |  | 10 | 1 | 10 | Nos.
19 | 16Sq.mm Power Terminal (Red) | Elmex |  | 1 | 1 | 1 | Nos.
20 | 16Sq.mm Power Terminal (Black) | Elmex |  | 1 | 1 | 1 | Nos.
21 | UTILITY SOCKET 5A universal | Anchor |  | 1 | 1 | 1 | Nos.
22 | Door Limit Switch | Kaycee |  | 2 | 1 | 2 | Nos.
23 | 5 Watt, Tubelight 230VAC supply voltage | Oreva |  | 2 | 1 | 2 | Nos.
24 | 6 Inch Air Filter | Elettro |  | 5 | 1 | 5 | Nos.
25 | 6 Inch Fan | Rexnord |  | 2 | 1 | 2 | Nos.
26 | Reset Push Button (Yellow) with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
27 | Hooter Acknowledge Push Button (Black) with NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
28 | E.STOP PB Mh. Type. With 1 NO Contact | Teknic |  | 1 | 1 | 1 | Nos.
29 | Hooter 230VAC | Shavison |  | 1 | 1 | 1 | Nos.
B | PLC SECTION |  |  | 1 | 1 | 1 | Nos.
1 | CPU-1512SP-1 PN FOR ET 200 SP | Siemens | 6ES75121DM030AB0 | 1 | 1 | 1 | Nos.
2 | PROFIBUS CARD | Siemens | 6ES75455DA000AB0 | 1 | 1 | 1 | Nos.
3 | SIMATIC ET 200SP, Digital input module, DI 16x 24V DC | Siemens | 6ES71316BH010BA0 | 7 | 1 | 7 | Nos.
4 | SIMATIC ET 200SP, Digital output module, DQ 16x 24V | Siemens | 6ES71326BH010BA0 | 4 | 1 | 4 | Nos.
5 | SIMATIC ET 200SP, analog input module, AI 8XU/I 2/4-wire basic | Siemens | 6ES71346GF000AA1 | 3 | 1 | 3 | Nos.
6 | SIMATIC ET 200SP, Analog output module, AQ 4XU/I | Siemens | 6ES71356HD000BA1 | 2 | 1 | 2 | Nos.
7 | SIMATIC ET 200SP, BaseUnit BU15-P16+A0+2D, BU type A0, push-in terminals | Siemens | 6ES71936BP000DA0 | 4 | 1 | 4 | Nos.
8 | SIMATIC ET 200SP, BaseUnit BU15-P16+A0+2B, BU type A0, Push-in terminals | Siemens | 6ES71936BP000BA0 | 12 | 1 | 12 | Nos.
9 | SIMATIC S7 MEMORY CARD 12 MB FOR PLC | Siemens | 6ES7954-8LE03-0AA0 | 1 | 1 | 1 | Nos.
10 | SIMATIC S7 MEMORY CARD 2GB FOR HMI | Siemens | 6AV21818XP000AX0 | 1 | 1 | 1 | Nos.
11 | SIMATIC HMI MTP1200 UNIFIED COMFORT | Siemens | 6AV21283MB060AX0 | 1 | 1 | 1 | Nos.
12 | Unmanaged Industrial Ethernet Switch | Siemens | 6GK50080BA101AB2 | 1 | 1 | 1 | Nos.
13 | 8 Channel 24VDC Relay Board | Omron |  | 8 | 1 | 8 | Nos.
14 | 2.5 Sq.mm Control Terminals | Elmex |  | 250 | 1 | 250 | Nos.
15 | Fuse Terminals | Elmex |  | 220 | 1 | 220 | Nos.
16 | 250mA Fuse | STD. |  | 40 | 1 | 40 | Mtrs
17 | 500mA Fuse | STD. |  | 105 | 1 | 105 | Nos.
18 | 2A Fuse | STD. |  | 75 | 1 | 75 | Nos.