## MOJJ MCC
PRG-2526-554-BOM FOR MCC PANEL
SR NO. | ITEM DESCRIPTIONS | MAKE | PART NO | ITEM QTY | FDR QTY | TOTAL QTY | UOM
A | MAIN INCOMER, MCCB 3P,200 AMP |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 3P,200 AMP, 50kA | Schneider | LV525452 | 1 | 1 | 1 | Nos.
2 | Extended door mounting handle | Schneider | LV429338_IN | 1 | 1 | 1 | Nos.
3 | Spreader Links | Schneider | LV431563 | 2 | 1 | 2 | Nos.
4 | 2A, 1P, 10kA, C-Curve MCB, for RYB indication lamps | Schneider | A9N1P02C | 3 | 1 | 3 | Nos.
5 | 6A, 1P, 10kA, C-Curve MCB | Schneider | A9N1P06C | 2 | 1 | 2 | Nos.
6 | 6A, 3P, 10kA, C-Curve MCB, | Schneider | A9N3P06C | 1 | 1 | 1 | Nos.
7 | 16A, 2P, 10kA, C-Curve MCB, | Schneider | A9N2P16C | 2 | 1 | 2 | Nos.
8 | Digital Ammeter (0-200 Amp) | Rishabh | - | 1 | 1 | 1 | Nos.
9 | Digital Voltmeter (0-500 Volt) | Rishabh | - | 1 | 1 | 1 | Nos.
10 | Ammeter Selecter Switch | Salzer | - | 1 | 1 | 1 | Nos.
11 | Voltmeter Selector Switch | Salzer | - | 1 | 1 | 1 | Nos.
12 | Digital MFM- EM 6436 With RS 485 Communication | Conzerv | EM 6436 | 1 | 1 | 1 | Nos.
13 | Current Transformer 200/5VA resin cast | Elmex | - | 3 | 1 | 3 | Nos.
14 | CTTB | Elmex | - | 4 | 1 | 4 | Nos.
15 | Loc/Rem Ssw 3Pos. | Salzer | - | 1 | 1 | 1 | Nos.
16 | Power contactor 3P,9Amp with coil voltage 230VAC (S) | Schneider | LC1D09 | 4 | 1 | 4 | Nos.
17 | 4NO Add On Block | Schneider | LADN40 | 2 | 1 | 2 | Nos.
18 | Red Indication Lamp, 230VAC supply voltage | Teknic | - | 1 | 1 | 1 | Nos.
19 | Yellow Indication Lamp, 230VAC supply voltage | Teknic | - | 1 | 1 | 1 | Nos.
20 | Blue Indication Lamp, 230VAC supply voltage | Teknic | - | 1 | 1 | 1 | Nos.
21 | Green Indication Lamp, 230VAC supply voltage | Teknic | - | 1 | 1 | 1 | Nos.
22 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 3 | 1 | 3 | Nos.
23 | Door Limit Switch | Kaycee | - | 2 | 1 | 2 | Nos.
24 | Tubelight 1ph 230VAC, 5W | Oreva | - | 2 | 1 | 2 | Nos.
25 | Fan 6"inch 230VAC with grill | Rexnord | - | 3 | 1 | 3 | Nos.
26 | Air Filter 6" | Ellettro | - | 6 | 1 | 6 | Nos.
27 | Neutral Link | STD. | - | 2 | 1 | 2 | Nos.
28 | Control Transformer 1.5kVA, 415/230VAC | Sahara | - | 1 | 1 | 1 | Nos.
B | MCC SECTION |  |  | 1 | 1 | 1 | Nos.
1 | VFD FEEDER 18.5 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 3P,100Amp | Schneider | LV510455 | 1 | 1 | 1 | Nos.
2 | Fuse Base 160AMP | Schneider | - | 3 | 1 | 3 | Nos.
3 | Fuse Link 50Amp | Schneider | - | 3 | 1 | 3 | Nos.
4 | VFD 18.5kW | ABB | (Customer Scope) | 1 | 1 | 1 | Nos.
5 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. | - | 1 | 1 | 1 | Nos.
7 | A/M ssw 2 Pos | Salzer |  | 1 | 1 | 1 | Nos.
8 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
9 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
10 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
11 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
12 | Aux. relay 4 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
13 | Yellow PB for Speed Increase | Teknic | - | 1 | 1 | 1 | Nos.
14 | Blue PB for Speed Decrease | Teknic | - | 1 | 1 | 1 | Nos.
15 | Power terminals 16Sq.mm, RYB | Elmex | - | 3 | 1 | 3 | Nos.
16 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 1 | 6 | Nos.
2 | VFD FEEDER 3.7 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
5 | 16A, 3P, 10kA, C-Curve MCB- Power supply | Schneider | A9N3P16C | 1 | 1 | 1 | Nos.
2 | Fuse Base 160AMP | Schneider | - | 3 | 1 | 3 | Nos.
3 | Fuse Link 10Amp | Schneider | - | 3 | 1 | 3 | Nos.
4 | VFD 3.7kW | ABB | (Customer Scope) | 1 | 1 | 1 | Nos.
5 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. | - | 1 | 1 | 1 | Nos.
7 | A/M ssw 2 Pos | Salzer |  | 1 | 1 | 1 | Nos.
8 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
9 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
10 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
11 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
12 | Aux. relay 4 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
13 | Yellow PB for Speed Increase | Teknic | - | 1 | 1 | 1 | Nos.
14 | Blue PB for Speed Decrease | Teknic | - | 1 | 1 | 1 | Nos.
15 | Power terminals 10Sq.mm, RYB | Elmex | - | 3 | 1 | 3 | Nos.
16 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 1 | 6 | Nos.
3 | VFD FEEDER 1.5 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
5 | 6A, 3P, 10kA, C-Curve MCB- Power supply | Schneider | A9N3P06C | 1 | 1 | 1 | Nos.
2 | Fuse Base 160AMP | Schneider | - | 3 | 1 | 3 | Nos.
3 | Fuse Link 10Amp | Schneider | - | 3 | 1 | 3 | Nos.
4 | VFD 1.5kW | ABB | (Customer Scope) | 1 | 1 | 1 | Nos.
5 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. | - | 1 | 1 | 1 | Nos.
7 | A/M ssw 2 Pos | Salzer |  | 1 | 1 | 1 | Nos.
8 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
9 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
10 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
11 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
12 | Aux. relay 4 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
13 | Yellow PB for Speed Increase | Teknic | - | 1 | 1 | 1 | Nos.
14 | Blue PB for Speed Decrease | Teknic | - | 1 | 1 | 1 | Nos.
15 | Power terminals 6Sq.mm, RYB | Elmex | - | 3 | 1 | 3 | Nos.
16 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 1 | 6 | Nos.
4 | S/D FEEDER 11 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 3P,50Amp | Schneider | LV510454 | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,32Amp with coil voltage 230VAC (M+D) | Schneider | LC1D32 | 1 | 1 | 1 | Nos.
3 | Power contactor 3P,12Amp with coil voltage 230VAC (S) | Schneider | LC1D12 | 2 | 1 | 2 | Nos.
4 | Overload Relay 6.4-32Amp (Class-30) | Schneider | LR9D32 | 1 | 1 | 1 | Nos.
5 | S/D timer 0-60 Sec | GIC | - | 1 | 1 | 1 | Nos.
6 | 3NO And 1NC contact block As per requirement | Schneider | LADN31 | 1 | 1 | 1 | Nos.
7 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
8 | Neutral Link | STD. | - | 1 | 1 | 1 | Nos.
9 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
10 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
11 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
12 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
13 | Power terminals 10Sq.mm, RYB | Elmex | - | 6 | 1 | 6 | Nos.
14 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 1 | 6 | Nos.
5 | S/D FEEDER 11 KW 2 NOS |  |  | 1 | 2 | 2 | Nos.
1 | MCCB 3P,50Amp | Schneider | LV510454 | 1 | 2 | 2 | Nos.
2 | Power contactor 3P,32Amp with coil voltage 230VAC (M+D) | Schneider | LC1D32 | 1 | 2 | 2 | Nos.
3 | Power contactor 3P,12Amp with coil voltage 230VAC (S) | Schneider | LC1D12 | 2 | 2 | 4 | Nos.
4 | Overload Relay 12-18Amp | Schneider | LRD21 | 1 | 2 | 2 | Nos.
5 | S/D timer 0-60 Sec | GIC | - | 1 | 2 | 2 | Nos.
6 | 3NO And 1NC contact block As per requirement | Schneider | LADN31 | 1 | 2 | 2 | Nos.
7 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 2 | 2 | Nos.
8 | Neutral Link | STD. | - | 1 | 2 | 2 | Nos.
9 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 2 | 2 | Nos.
10 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 2 | 2 | Nos.
11 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 2 | 2 | Nos.
12 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 2 | 2 | Nos.
13 | Power terminals 10Sq.mm, RYB | Elmex | - | 6 | 2 | 12 | Nos.
14 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 2 | 12 | Nos.
6 | DOL FEEDER 3.7 KW 2 NOS |  |  | 1 | 2 | 2 | Nos.
1 | 16A, 3P, 10kA, C-Curve MCB- Power supply | Schneider | A9N3P16C | 1 | 2 | 2 | Nos.
2 | Power contactor 3P,12Amp with coil voltage 230VAC | Schneider | LC1D12 | 1 | 2 | 2 | Nos.
3 | Overload Relay 7-10A | Schneider | LRD14 | 1 | 2 | 2 | Nos.
4 | 3NO And 1NC contact block As per requirement | Schneider | LADN31 | 1 | 2 | 2 | Nos.
5 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 2 | 2 | Nos.
6 | Neutral Link | STD. | - | 1 | 2 | 2 | Nos.
7 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 2 | 2 | Nos.
8 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 2 | 2 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 2 | 2 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 2 | 2 | Nos.
11 | Power terminals 10Sq.mm, RYB | Elmex | - | 3 | 2 | 6 | Nos.
12 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 2 | 12 | Nos.
7 | DOL FEEDER 0.75 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 6A, 3P, 10kA, C-Curve MCB- Power supply | Schneider | A9N3P06C | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 1 | 1 | Nos.
3 | Overload Relay 1.6-2.5A | Schneider | LRD07 | 1 | 1 | 1 | Nos.
4 | 3NO And 1NC contact block As per requirement | Schneider | LADN31 | 1 | 1 | 1 | Nos.
5 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. | - | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
11 | Power terminals 6Sq.mm, RYB | Elmex | - | 3 | 1 | 3 | Nos.
12 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 1 | 6 | Nos.
8 | DOL FEEDER 0.17 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 6A, 3P, 10kA, C-Curve MCB- Power supply | Schneider | A9N3P06C | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 1 | 1 | Nos.
3 | Overload Relay 0.63-1A | Schneider | LRD05 | 1 | 1 | 1 | Nos.
4 | 3NO And 1NC contact block As per requirement | Schneider | LADN31 | 1 | 1 | 1 | Nos.
5 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
6 | Neutral Link | STD. | - | 1 | 1 | 1 | Nos.
7 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
8 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
9 | Trip (Amber) Indication lamp, 230VAC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
11 | Power terminals 6Sq.mm, RYB | Elmex | - | 3 | 1 | 3 | Nos.
12 | Control terminals 4Sq.mm, Gray | Elmex | - | 6 | 1 | 6 | Nos.
6 | SUPPLY FEEDER (BURNER MOTOR ) 0.75 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 6A, 4P, 10kA, C-Curve MCB | Schneider | A9N4P06C | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 1 | 1 | Nos.
3 | 6A, 1P, 10kA, C-Curve MCB | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
4 | 2A, 1P, 10kA, C-Curve MCB | Schneider | A9N1P02C | 1 | 1 | 1 | Nos.
5 | PID Controller (NEX-605) | RADIX | (Customer Scope) | 1 | 1 | 1 | Nos.
6 | Stop PB Mh. Head | Teknic | 2AM4 | 1 | 1 | 1 | Nos.
7 | Neutral Link | STD. | - | 1 | 1 | 1 | Nos.
8 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 1 | 1 | 1 | Nos.
9 | Amber Trip Indication lamp 230VAC supply voltage | Teknic | - | 1 | 1 | 1 | Nos.
10 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 4 | 1 | 4 | Nos.
11 | Power Terminals 6 SQMM R/Y/B/N | Elmex | - | 4 | 1 | 4 | Nos.
12 | Fuse Terminal | Elmex | - | 1 | 1 | 1 | Nos.
13 | Control terminals 4Sq.mm, Gray | Elmex | - | 14 | 1 | 14 | Nos.
7 | SUPPLY FEEDER 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 16A, 4P, 10kA, C-Curve MCB | Schneider | A9N4P16C | 1 | 1 | 1 | Nos.
2 | Fuse Terminals with 2Amp Fuse | Elmex | - | 1 | 1 | 1 | Nos.
3 | ON (GREEN) Indication lamp, 24VDC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
4 | Power Terminals 6 SQMM R/Y/B/N | Elmex | - | 4 | 1 | 4 | Nos.
8 | SUPPLY FEEDER 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 10A, 2P, 10kA, C-Curve MCB | Schneider | A9N2P10C | 1 | 1 | 1 | Nos.
2 | Fuse Terminals with 2Amp Fuse | Elmex | - | 1 | 1 | 1 | Nos.
3 | ON (GREEN) Indication lamp, 24VDC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
4 | Power Terminals 6 SQMM R/N | Elmex | - | 4 | 1 | 4 | Nos.
9 | SUPPLY FEEDER 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 6A, 2P, 10kA, C-Curve MCB | Schneider | A9N2P06C | 1 | 1 | 1 | Nos.
2 | Fuse Terminals with 2Amp Fuse | Elmex | - | 1 | 1 | 1 | Nos.
3 | ON (GREEN) Indication lamp, 24VDC supply voltage | Teknic | 3PLBR5L | 1 | 1 | 1 | Nos.
4 | Power Terminals 6 SQMM R/N | Elmex | - | 4 | 1 | 4 | Nos.
10 | HAMMER 230VAC SUPPLY |  |  | 1 | 8 | 8 | Nos.
1 | 6A, 2P, 10kA, C-Curve MCB- Power supply | Schneider | A9N2P06C | 8 | 1 | 8 | Nos.
2 | 6A, 1P, 10kA, C-Curve MCB- Control supply | Schneider | A9N1P06C | 1 | 1 | 1 | Nos.
3 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 8 | 1 | 8 | Nos.
4 | Start (Green) Illuminated Push button | Teknic | 2ALRF3 | 8 | 1 | 8 | Nos.
5 | SSW 3 Position | Salzer |  | 2 | 1 | 2 | Nos.
6 | Aux. relay 2 c/o with base & pin, 230VAC | Omron | - | 1 | 1 | 1 | Nos.
7 | Fuse Terminals with 2Amp Fuse | Elmex | - | 2 | 1 | 2 | Nos.
8 | Control terminals 4Sq.mm, Gray | Elmex | - | 4 | 1 | 4 | Nos.
9 | 10 Point Sequential Timer | EAPL | - | 1 | 1 | 1 | Nos.
C | PLC SECTION |  |  | 1 | 1 | 1 | Nos.
1 | 8 SLOTS BACKPLANE | Schneider | BMXXBP0800 | 1 | 1 | 1 | Nos.
2 | STANDARD AC POWER SUPPLY | Schneider | BMXCPS2000 | 1 | 1 | 1 | Nos.
3 | CPU340-20 MODBUS ETHERNET | Schneider | BMXP342020 | 1 | 1 | 1 | Nos.
4 | DIG 32I 24 VDC SINK | Schneider | BMXDDI3202K | 2 | 1 | 2 | Nos.
5 | FCN 2 X 20 WIRE 3M CABLE | Schneider | BMXFCW303 | 3 | 1 | 3 | Nos.
6 | DIG 32Q TRANS SOURCE 0.1A | Schneider | BMXDDO3202K | 1 | 1 | 1 | Nos.
7 | Ana 8 U/I In No Isol Fast | Schneider | BMXAMI0800 | 2 | 1 | 2 | Nos.
8 | CAGED TERMINAL STRIP 28 POINTS | Schneider | BMXFTB2800 | 2 | 1 | 2 | Nos.
9 | Ana 8 Current Out No Isol | Schneider | BMXAMO0802 | 1 | 1 | 1 | Lot
10 | SCREW TERMINAL STRIP 20 POINTS | Schneider | BMXFTB2010 | 1 | 1 | 1 | Lot
11 | 10"W Easy Touch Panel, Ethernet model | Schneider | HMIET6500 | 1 | 1 | 1 | Lot
D | PLC Control SECTION |  |  | 1 | 1 | 1 | Nos.
1 | 32A, 2P, 10kA,B36 MCB | Schneider | A9N2P32C | 1 | 1 | 1 | Nos.
2 | 6A, 2P, 10kA, C-Curve MCB, | Schneider | A9N2P06C | 5 | 1 | 5 | Nos.
3 | 10A, 2P, 10kA, C-Curve MCB, | Schneider | A9N2P10C | 1 | 1 | 1 | Nos.
4 | 6A, 1P, 10kA, C-Curve MCB | Schneider | A9N1P06C | 6 | 1 | 6 | Nos.
5 | SMPS 5A 24VDC POWER SUPPLY | Meanwell | - | 2 | 1 | 2 | Nos.
6 | Diode Module 10A, 24VDC | Meanwell | - | 1 | 1 | 1 | Nos.
7 | Fuse Terminals with 2Amp Fuse | Elmex | - | 3 | 1 | 3 | Nos.
8 | Fuse Terminals with 2Amp Fuse (Indication Type) | Elmex | - | 10 | 1 | 10 | Nos.
9 | ON (GREEN) Indication lamp, 230VAC supply voltage | Teknic |  | 1 | 1 | 1 | Nos.
10 | ON (GREEN) Indication lamp, 24VDC supply voltage | Teknic |  | 2 | 1 | 2 | Nos.
11 | 24 VDC Ethernet Switch | STD. | - | 1 | 1 | 1 | Nos.
12 | 8 Channel 24VDC Relay Board | Omron | - | 4 | 1 | 4 | Nos.
13 | E-Stop PB Mh. Head with NC Contact | Teknic | - | 1 | 1 | 1 | Nos.
14 | AlarmAccept Yellow PB with NO Contact | Teknic | - | 1 | 1 | 1 | Nos.
15 | Hooter 24VDC | Shavison | - | 1 | 1 | 1 | Nos.
16 | Fuse Terminals | Elmex | - | 80 | 1 | 80 | Nos.
17 | 250mA Fuse | STD. | - | 20 | 1 | 20 | Mtrs
18 | 500mA Fuse | STD. | - | 32 | 1 | 32 | Nos.
19 | 2A Fuse | STD. | - | 20 | 1 | 20 | Nos.
20 | Power terminals 6Sq.mm, R/N | Elmex | - | 2 | 1 | 2 | Nos.
21 | Control terminals 4Sq.mm, Gray | Elmex | - | 80 | 1 | 80 | Nos.
E | SUPPLY TO HMI |  |  | 1 | 1 | 1 | Nos.
1 | 6A, 2P, 10kA, C-Curve MCB, | Schneider | A9N2P06C | 2 | 1 | 2 | Nos.
2 | 230VAC On Indication (RED) | Teknic | 3PLBR4L | 1 | 1 | 1 | Nos.
3 | 24VDC On Indication (GREEN) | Teknic | 3PLBR3L | 1 | 1 | 1 | Nos.
4 | SMPS 5A 24VDC POWER SUPPLY | Meanwell | - | 1 | 1 | 1 | Nos.
5 | E-Stop PB Mh. Head with NC Contact | Teknic | - | 1 | 1 | 1 | Nos.