## BOM-637-MCC+PLC PANEL
PROJECT:- PRG-2526-637-ASEE-MARVEL-375KLD PLC+MCC |  |  |  | REV-R0
CLIENT:- |  |  |  | Issued For Approval
DOCUMENT NO:-
DATE:-03-01-2026 |  | PREPARED BY | T.A.
|  | CHECKED BY | V.K.
PRG-2526-637-BOM
SR NO. | ITEM DESCRIPTIONS | MAKE | PART NO | ITEM QTY | FDR QTY | TOTAL QTY | UOM
A | MAIN INCOMER, MCCB 3P,63 AMP |  |  | 1 | 1 | 1 | Nos.
1 | MCCB 3P, 63AMP, 36kA, TMD | Schneider | LV510335 | 1 | 1 | 1 | Nos.
2 | Extended Rotary Handle | Schneider | LV429338_IN | 1 | 1 | 1 | Nos.
3 | FTB for RYB indication 2A | STD. |  | 3 | 1 | 3 | Nos.
4 | Fuse TB 6A | STD. |  | 1 | 1 | 1 | Nos.
5 | 6A, 3P, 10kA, C-Curve MCB, | Schneider | A9N3P06C | 1 | 1 | 1 | Nos.
6 | 6A,2P, 10kA, C-Curve MCB | Schneider | A9N2P06C | 3 | 1 | 3 | Nos.
7 | 10A, 2P, 10kA, C-Curve MCB | Schneider | A9N2P10C | 1 | 1 | 1 | Nos.
8 | Digital MFM-With RS 485 Communication | Selec | - | 1 | 1 | 1 | Nos.
9 | Current Transformer 60/5A 5 VA | Elmex |  | 3 | 1 | 3 | Nos.
10 | Red Indication Lamp, 230VAC supply voltage | Teknic | 3PLBR4L | 1 | 1 | 1 | Nos.
11 | Yellow Indication Lamp, 230VAC supply voltage | Teknic | 3PLBR8L | 1 | 1 | 1 | Nos.
12 | Blue Indication Lamp, 230VAC supply voltage | Teknic | 3PLBR6L | 1 | 1 | 1 | Nos.
13 | Door Limit Switch | Kaycee |  | 1 | 1 | 1 | Nos.
14 | Tubelight 230VAC,5W | Oreva |  | 1 | 1 | 1 | Nos.
15 | Fan 6"inch 230VAC | Rexnord |  | 2 | 1 | 2 | Nos.
16 | Air Filter 6" | Ellettro |  | 4 | 1 | 4 | Nos.
17 | Control Transfomer 415/230VAC-750 VA | Sahara |  | 1 | 1 | 1 | Nos.
18 | Utility Socket 230VAC,5Amp | Anchor |  | 1 | 1 | 1 | Nos.
19 | CTTB | STD. |  | 4 | 1 | 4 | Nos.
20 | SMPS 10 Amp, 24VDC | Meanwell |  | 1 | 1 | 1 | Nos.
21 | DBK | Elmex |  | 2 | 1 | 2 | Nos.
22 | Power terminals 16Sq.mm, RYB | Elmex |  | 5 | 1 | 5 | Nos.
23 | Power cable 10Sq.mm, RYB | Polycab |  | 1 | 1 | 1 | Lot
24 | TB flag | Elmex | - | 1 | 1 | 1 | Lot
25 | Stopper | Elmex | - | 1 | 1 | 1 | Lot
26 | TB Marker | Elmex | - | 1 | 1 | 1 | Lot
27 | End plate | Elmex | - | 1 | 1 | 1 | Lot
1 | DOL FEEDER 0.18 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 6A, 3P, 10kA, C-Curve MCB | Schneider | A9N3P06C | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 1 | 1 | Nos.
3 | Overload Relay (0.4-0.63A) | Schneider | LRD04 | 1 | 1 | 1 | Nos.
4 | L/R 3 Position ILSW | Teknic |  | 1 | 1 | 1 | Nos.
5 | Power terminals 6Sq.mm, RYB | Elmex |  | 3 | 1 | 3 | Nos.
6 | Power cable 2.5Sq.mm, RYB | Polycab |  | 1 | 1 | 1 | Lot
2 | DOL FEEDER 1.5 KW 5 NOS |  |  | 1 | 5 | 5 | Nos.
1 | 10A, 3P, 10kA, C-Curve MCB | Schneider | A9N3P10C | 1 | 5 | 5 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 5 | 5 | Nos.
3 | Overload Relay 2.5-4A | Schneider | LRD08 | 1 | 5 | 5 | Nos.
4 | L/R 3 Position ILSW | Teknic |  | 1 | 5 | 5 | Nos.
5 | Power terminals 6Sq.mm, RYB | Elmex |  | 3 | 5 | 15 | Nos.
6 | Power cable 2.5Sq.mm, RYB | Polycab |  | 1 | 5 | 5 | Lot
3 | DOL FEEDER 2.2 KW 4 NOS |  |  | 1 | 4 | 4 | Nos.
1 | 16A, 3P, 10kA, C-Curve MCB | Schneider | A9N3P16C | 1 | 4 | 4 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 4 | 4 | Nos.
3 | Overload Relay 4-6A | Schneider | LRD10 | 1 | 4 | 4 | Nos.
4 | L/R 3 Position ILSW | Teknic |  | 1 | 4 | 4 | Nos.
5 | Power terminals 6Sq.mm, RYB | Elmex |  | 3 | 4 | 12 | Nos.
6 | Power cable 2.5Sq.mm, RYB | Polycab |  | 1 | 4 | 4 | Lot
4 | DOL FEEDER 2.2 KW 1 NOS |  |  | 1 | 1 | 1 | Nos.
1 | 16A, 3P, 10kA, C-Curve MCB | Schneider | A9N3P16C | 1 | 1 | 1 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 1 | 1 | Nos.
3 | Overload Relay 4-6A | Schneider | LRD10 | 1 | 1 | 1 | Nos.
4 | ON/OFF 2 Position ILSW | Teknic |  | 1 | 1 | 1 | Nos.
5 | Power terminals 6Sq.mm, RYB | Elmex |  | 3 | 1 | 3 | Nos.
6 | Power cable 2.5Sq.mm, RYB | Polycab |  | 1 | 1 | 1 | Lot
5 | DOL FEEDER 0.37 KW 2 NOS |  |  | 1 | 2 | 2 | Nos.
1 | 6A, 3P, 10kA, C-Curve MCB | Schneider | A9N3P06C | 1 | 2 | 2 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 2 | 2 | Nos.
3 | Overload Relay 1-1.6A | Schneider | LRD06 | 1 | 2 | 2 | Nos.
4 | L/R 3 Position ILSW | Teknic |  | 1 | 2 | 2 | Nos.
5 | Power terminals 6Sq.mm, RYB | Elmex |  | 3 | 2 | 6 | Nos.
6 | Power cable 2.5Sq.mm, RYB | Polycab |  | 1 | 2 | 2 | Lot
6 | DOL FEEDER 3.7 KW 6 NOS |  |  | 1 | 6 | 6 | Nos.
1 | 16A, 3P, 10kA, C-Curve MCB | Schneider | A9N3P16C | 1 | 6 | 6 | Nos.
2 | Power contactor 3P,25Amp with coil voltage 230VAC | Schneider | LC1D25 | 1 | 6 | 6 | Nos.
3 | Overload Relay 7-10A | Schneider | LRD14 | 1 | 6 | 6 | Nos.
4 | L/R 3 Position ILSW | Teknic |  | 1 | 6 | 6 | Nos.
5 | Power terminals 6Sq.mm, RYB | Elmex |  | 3 | 6 | 18 | Nos.
6 | Power cable 2.5Sq.mm, RYB | Polycab |  | 1 | 6 | 6 | Lot
7 | S/D FEEDER 15 KW 2 NOS |  |  | 1 | 2 | 2 | Nos.
1 | MCB 3P, 63AMP | Schneider | A9N3P63C | 1 | 2 | 2 | Nos.
2 | Power contactor 3P,40Amp with coil voltage 230VAC (M+D) | Schneider | LC1D40A | 2 | 2 | 4 | Nos.
3 | Power contactor 3P,18Amp with coil voltage 230VAC (S) | Schneider | LC1D18 | 1 | 2 | 2 | Nos.
4 | Overload Relay 12-18 Amp | Schneider | LRD21 | 1 | 2 | 2 | Nos.
5 | Overload Mounting Kit | Schneider | LAD7B106 | 1 | 2 | 2 | Nos.
6 | 1NO And 1NC contact block As per requirement | Schneider | LADN11 | 3 | 2 | 6 | Nos.
7 | S/D timer 0-60 Sec | GIC |  | 1 | 2 | 2 | Nos.
8 | L/R 3 Position ILSW | Teknic |  | 1 | 2 | 2 | Nos.
9 | Power terminals 16Sq.mm, | Elmex |  | 6 | 2 | 12 | Nos.
10 | Power cable 10 Sq.mm, RYB | Polycab |  | 1 | 2 | 2 | Lot
11 | Power cable 6Sq.mm, RYB | Polycab |  | 1 | 2 | 2 | Lot
8 | DOL FEEDER 0.75 KW 2 NOS |  |  | 1 | 2 | 2 | Nos.
1 | 6A, 3P, 10kA, C-Curve MCB | Schneider | A9N3P06C | 1 | 2 | 2 | Nos.
2 | Power contactor 3P,9Amp with coil voltage 230VAC | Schneider | LC1D09 | 1 | 2 | 2 | Nos.
3 | Overload Relay 1.6-2.5A | Schneider | LRD07 | 1 | 2 | 2 | Nos.
4 | L/R 3 Position ILSW | Teknic |  | 1 | 2 | 2 | Nos.
5 | Power terminals 6Sq.mm, RYB | Elmex |  | 3 | 2 | 6 | Nos.
6 | Power cable 2.5Sq.mm, RYB | Polycab |  | 1 | 2 | 2 | Lot
9 | SUPPLY FEEDER |  |  | 1 | 1 | 1 | Nos.
1 | 6A,2P, 10kA, C-Curve MCB | Schneider | A9N2P06C | 4 | 1 | 4 | Nos.
2 | 10A,2P, 10kA, C-Curve MCB | Schneider | A9N2P10C | 1 | 1 | 1 | Nos.
3 | L/R 3 Position ILSW | Teknic |  | 4 | 1 | 4 | Nos.
4 | Power Earthing terminals 4Sq.mm | Elmex |  | 12 | 1 | 12 | Nos.
5 | Power terminals 6Sq.mm RED | Elmex |  | 2 | 1 | 2 | Nos.
6 | Power terminals 6Sq.mm YELLOW | Elmex |  | 9 | 1 | 9 | Nos.
7 | Power terminals 6Sq.mm BLUE | Elmex |  | 1 | 1 | 1 | Nos.
8 | Power terminals 6Sq.mm BLACK | Elmex |  | 12 | 1 | 12 | Nos.
PLC SECTION
1 | PLC CPU DVP-SA, 8 DI/4DO | Delta | DVP12SA211R | 1 | 1 | 1 | Nos.
2 | Digital Input Module 16 DI CARD | Delta | DVP16SM11N | 4 | 1 | 4 | Nos.
3 | Digital Output Module 16 DO CARD | Delta | DVP16SN11T | 2 | 1 | 2 | Nos.
4 | Analog Input Module 4 AI CARD | Delta | DVP04AD-S | 2 | 1 | 2 | Nos.
5 | HMI 7 Inch | Delta | DOP-107CV | 1 | 1 | 1 | Nos.
6 | Relay Board 4 Channel 1c/o | OMRON |  | 1 | 1 | 1 | Nos.
7 | Relay Board 8 Channel 1c/o | OMRON |  | 4 | 1 | 4 | Nos.
8 | Loc/Rem SSW 2 Pos. | Teknic |  | 1 | 1 | 1 | Nos.
9 | Alarm Accept PB Yellow | Teknic |  | 1 | 1 | 1 | Nos.
10 | Emg Stop | Teknic |  | 1 | 1 | 1 | Nos.
11 | Hooter | Shavison |  | 1 | 1 | 1 | Nos.
12 | Control Terminals 4 Sqmm Fuse Type | Elmex |  | 50 | 1 | 50 | Nos.
13 | Fuse- 2A, 250mA, 500mA | Elmex |  | 50 | 1 | 50 | Nos.
14 | Control Terminals 2.5Sq.mm Non-Fuse | Elmex |  | 60 | 1 | 60 | Nos.